#

**PRODUCT BENEFITS**

* Prolongs equipment life; reduces maintenance and replacement costs
* Provides energy savings by maintaining efficient heat transfer surfaces
* Inhibits corrosion and pitting, reducing resultant tube failures
* Virtually eliminates the need for harsh boiler chemical or mechanical cleanings

**PRODUCT SAFETY INFORMATION**

This is an alkaline product that can irritate the skin and eyes and should be handled accordingly. Gloves, goggles and an apron are recommended. Anyone responsible for the procurement, use, or testing of this product should familiarize themselves with the appropriate safety and handling precautions involved. Such information is outlined in the Safety Data Sheet. In an emergency, contact *Brody Chemical*, day or night, at (801) 963-2436.

**SHIPPING**

We package this product in 5-gallon pails containing 43 pounds net weight, 55-gallon drums holding 470 pounds net, or in 275-gallon totes that carry 2350 pounds net. Bulk quantities (1000-5000 gallons) are also available.

**USDA / FDA**

B601 complies with USDA Category G6 requirements and with FDA CFR Title 21 §173.310 regulations pertaining to boiler water additives where steam contacts food, milk, or milk products.

**ADDITIONAL INFORMATION**

To obtain any other technical product information or to place an order, call *Brody Chemical* at (801) 963-2436. Alternately, you may e-mail us at orders@brodychemical.com or write us at 6125 W Double Eagle Circle, Salt Lake City, UT 84118.

### PRINCIPAL USES

This product is formulated as a liquid sulfite boiler water treatment. It is designed to provide pitting and corrosion protection as a separate component. It performs well with either hard or soft water makeup. Use this product in steam boilers in concert with dispersants, phosphates and alkalinity booster, up to a maximum operating pressure of 1500 psi.

B601 incorporates proven chemical technology to achieve superior oxygen scavenging which results in excellent corrosion inhibition. It can maintain clean and corrosion free boilers during normal operation, thus preventing costly shut downs to clean the boiler.

**PREPARATION AND FEEDING**

Inject B601 directly into the storage section of the deaerator or the boiler feedwater line. You may mix this product with other component products before feeding into the system. The interruption of chemical feed will result in corrosion in the boiler, decreased efficiency and possible tube failures. Slug feeding provides excellent results if performed very consistently in small to medium sized boilers when no metering pump exists.

Use chemical feed equipment constructed of stainless steel or plastic for this product. A successful treatment program using B601 should generally include separate component treatments of dispersants, phosphates, and alkalinity builder, and a condensate treatment product.

**DOSAGE**

The designed feed rate for this product is 150 ppm in the boiler water. Please consult your *Brody Chemical* water treatment specialist before commencing feed. The actual required dosage may vary depending upon operating frequency, feedwater quality and temperature, system loads, and percentage of condensate returned.

All statements, information, and data given herein are, to the best of our knowledge, accurate and reliable, but may not be complete. Brody Chemical furnishes this information in good faith, and unless specifically stated, without guarantee, warranty, or responsibility, expressed or implied. The user should not assume that all safety measures are indicated or that other measures may not be required.

#### **B601** Oxygen Scavenger